ITU    CIVIL ENGINEERING FACULTY

WATER SUPPLY AND ENVIRONMENTAL SANITATION

###### RECITATION 6 —

###### WATER DISTRIBUTION NETWORKS

1st Question:

P = 5000 and max qday = 200 l/ind./day

a) max Qhour = 5000 * 1.5 * 200 / 86400 =17.36 l/s

Li = 1.4*250 +1*400 = 750 m so, distribution discharge per unit length is:

q = 17.36/750 =0.0231 l/s/m.

Qcon1 = q * Li1 = 0.0231 * (1.4*250) = 8.10 l/s

Qcon2 = q * Li2 = 0.0231 * (1.0*400) = 9.26 l/s	These are the consumption (distributed) discharges.

When we multiply the consuption discharges for each pipe by 0.577 and add a constant fire discharge as 5.0 l/s, we reach the equivalent (calculation) discharges:

C1 = 8.10*0.557 + 5.0 = 9.67 l/s

C2 = 9.26*0.557 + 5.0 = 10.34 l/s

b) If the location of the dead point is right,  condition must be satisfied.

V1= C1/(D12/4) = 1.21 m/s	hl1 = f*V12*L1/(D1*2g) =0.03*1.212*250/(0.10*2*9.81) = 5.8 m

V2= C2/(D22/4) = 1.08 m/s	hl2 = f*V22*L2/(D2*2g) =0.03*1.082*400/(0.11*2*9.81) = 6.6 m

√  OK

So the head losses are close enough to be considered as equal. Thus, the location of the dead point is convenient with the diameters.

2nd Question:

CABC = 0.577 * 0.05 = 0.0288 m3/s

IMPORTANT NOTE: Under normal operating conditions we take fire discharge as zero. If the fire discharge is not given to you, you can also take it as zero.

VABC = 0.0288*4/(*0.22) = 0.92 m/s		hl ABC = 0.03*0.922/(0.2*2*9.81) = 2.9 m

Theoritically hl ABC = hl ADC, so		hl ADC = 0.03*VADC2/(0.2*2*9.81) = 2.9 m

From here V = 0.84 m/s

So the equivalent discharge of ADC pipe is:

CADC = 0.84 * (*0.32) = 0.06 m3/s =60 l/s

3rd Question:

hl BA = 5 m, hl CA = 9.5 m, PAB = PAC = 4000 ind., PHA = 6000 ind.

max qdayr =300 l/ind./day, (P/)min. = 20 m.

Qcon BA = Qcon CA =1.5 * 300 * 4000 / 86400 = 20.83 l/s

Qcon HA =1.5 * 300 * 6000 / 86400 = 31.25 l/s

We have to calculate the head loss for AH pipe:

CAH = 2*20.83 + 0.55*31.25 = 58.85 l/s

VAH = 0.05885*4/(0.32) = 0.832 m/s

hl HA = 0.03*0.8322*500 /(0.3*2*9.81) = 1.7 m

Now we have to determine the reservoir elevation with respect to all three, A-B-C, and take the maximum of all three as the minimum required reservoir surface elevation.

With respect to A: zH = 120 + 20 + 1.7 = 141.7 m

With respect to B: zH = 90 + 20 + 5 + 1.7 = 116.7 m

With respect to C: zH = 80 + 20 + 9.5 + 1.7 = 111.7 m

Thus, the minimum required reservoir elevation is 141.7 m.

# Text boxes

B(90)

H

A

D=300mm L=500m

D

B

D2=300mm L2=800m

D1=200mm L1=450m

C

A

B

D1=100mm L1=250m

k=1,4

D2=110mm L2=400m

k=1,0

C (80)

A (120)