ITU    CIVIL ENGINEERING FACULTY

WATER SUPPLY AND ENVIRONMENTAL SANITATION

###### RECITATION 5 —SOLUTIONS

###### DESIGN OF RESERVOIRS

###### TO COMPANSATE CONSUMPTION FLUCTUATIONS

The calculations are shown in the following table. The maximum difference between incoming volume and outgoing volume is seen at 08:00 which is 13%.That is why the cumulative incoming volume is increased by 13% to be the corrected cumulative incoming volume. The maximum water volume that is seen to be accumulating in the reservoir is appeared to be 39% which occurs at 18:00. Simply by multiplying by max.Qday;

max. Qday =  x mean qday x P = 1.5 x 150 x 100 000 x 10-3 = 22500 m3/day;

Vreservoir = 0.39 x 22500 = 8775 m3	.

| Time (o’clock) | Cumulative Vout (%) | Cumulative Vin (%) | Corrected Cumulative V’in (%) | V’in - Vout (%) |
| --- | --- | --- | --- | --- |
| 0 | 0 | 0 | 13 | 13 |
| 1 | 2 | 0 | 13 | 11 |
| 2 | 3 | 0 | 13 | 10 |
| 3 | 3.5 | 0 | 13 | 9.5 |
| 4 | 4 | 0 | 13 | 9 |
| 5 | 4.5 | 0 | 13 | 8.5 |
| 6 | 7 | 0 | 13 | 6 |
| 7 | 10 | 0 | 13 | 3 |
| 8 | 13 | 0 | 13 | 0 |
| 9 | 17 | 10 | 23 | 6 |
| 10 | 23 | 20 | 33 | 10 |
| 11 | 27 | 30 | 43 | 16 |
| 12 | 34.5 | 40 | 53 | 18.5 |
| 13 | 45.5 | 50 | 63 | 17.5 |
| 14 | 54 | 60 | 73 | 19 |
| 15 | 61 | 70 | 83 | 22 |
| 16 | 66 | 80 | 93 | 27 |
| 17 | 69 | 90 | 103 | 34 |
| 18 | 74 | 100 | 113 | . 39 . |
| 19 | 79 | 100 | 113 | 34 |
| 20 | 84 | 100 | 113 | 29 |
| 21 | 91 | 100 | 113 | 22 |
| 22 | 96 | 100 | 113 | 17 |
| 23 | 98 | 100 | 113 | 15 |
| 24 | 100 | 100 | 113 | 13 |